## FGRIO-FGR2IO series
Register Type | Register discription/register | User Inputs |  | Scale Factor | Unit of measure | 16bit Result |  | 20bit Result
Input | Analog In-put 1 (30001 msb) |  | Register value | 0.00015259 | Volts | 0 | Volts | 0 | Volts
|  |  | VDC | 0.00015259 | Volts | 0 | Register Value
| Analog In-put 1 (30002 lsb) |  | Register value | 2.3283e-09 | Volts | 0 | Volts
Conversion AI 1 | Resistor Value | 249 | Ohms |  |  | 0 | Miliamps
Input | Analog In-put 2 (30003 msb) |  | Register value | 0.00015259 | Volts | 0 | Volts | 0 | Volts
|  |  | VDC | 0.00015259 | Volts | 0 | Register Value
| Analog In-put 2 (30004 lsb) |  | Register value | 2.3283e-09 | Volts | 0 | Volts
Conversion AI 2 | Resistor Value | 249 | Ohms |  |  | 0 | Miliamps
Input | Analog In-put 3 (30016) |  | Register value | 5.3406e-05 | Volts | 0 | Volts
|  |  | VDC | 5.3406e-05 | Volts | 0 | Register Value
Conversion AI 3 | Resistor Value | 124 | Ohms |  |  | 0 | Miliamps
Input | Analog In-put 4 (30017) |  | Register value | 5.3406e-05 | Volts | 0 | Volts
|  |  | VDC | 5.3406e-05 | Volts | 0 | Register Value
Conversion AI 4 | Resistor Value | 124 | Ohms |  |  | 0 | Miliamps
Input | Input Voltage (30009) |  | Register value | 0.03262 | Volts | 0 | Volts
|  |  | VDC | 0.03262 | Volts | 0 | Register Value
Holding | Analog Output (40007) | 50000 | Register value | 0.00033569 | Amps | 16.7847 | Milli Amps
|  |  | Milli Amps | 0.00033569 | Amps | 0 | Register Value
Holding | Analog Output (40007) |  | Register value | 0.00033569 | Amps | 0 | Milli Amps
|  |  | Milli Amps | 0.00033569 | Amps | 0 | Register Value
Conversions | [5 empty] | In a calculator multiply the appropriate value below by the value in the Modbus register
| Enter Value of user manual here> |  |  | 0.001 |  | 0 | Milli (mV)
|  |  |  | 1e-06 |  | 0 | Micro (uV)
|  |  |  | 1e-09 |  | 0 | Nano (nV)